7000 VERTICAL TURBINE PUMP SPECIFICATIONS

ENCLOSED LINESHAFT CONSTRUCTION – OIL LUBRICATED

PART 1. GENERAL

  - This specification includes the supply of ____ vertical turbine oil lubricated enclosed lineshaft pump(s).  Each unit shall include a bowl assembly, suction strainer, column, lineshaft, enclosing tube, discharge head, sealing assembly and driver.

1.02	QUALITY ASSURANCE

- All pumping equipment furnished under this Section shall be of a design and manufacture that has been used in similar applications, and it shall be demonstrated to the satisfaction of the Owner that the quality is equal to equipment made by that manufacturer specifically named herein.

- Unit responsibility.  Pump(s), complete with motor, necessary guards and all other specified accessories and appurtenances shall be furnished by the pump manufacturer to insure compatibility and integrity of the individual components, and provide the specified warranty for all components.

- The vertical turbine pump(s) specified in this section shall be furnished by and be the product of one manufacturer.

- Pumps are to be engineered and manufactured under a written Quality Assurance program.  The Quality Assurance program is to be in effect for at least ten years, to include a written record of periodic internal and external audits to confirm compliance with such program.

- Pump(s) are to be engineered and manufactured under the certification of ISO-9001:2000.

  - PERFORMANCE

- The pump(s) shall be designed for continuous operation and will be operated continuously under normal service.

- OPERATION CRITERIA

|  | Flow (GPM) | TDH (ft.) | Max. Pump Speed (RPM) | Max. Solids Passage | Max. Shutoff Head (ft.) | Minimum Submergence (inches) |
| --- | --- | --- | --- | --- | --- | --- |
| Design Condition |  |  |  |  |  |  |
| Secondary Condition |  |  |  |  |  |  |

- Total dynamic head shall be as measured at the discharge of the pump and shall include velocity head and vertical static head from the minimum water level to the centerline of the pump discharge.

- Minimum water level shall be at elevation ________ feet.

- Pump(s) are to be mounted at _________ feet elevation with the sump floor at _________ feet elevation.

- Pump discharge centerline shall be at _________feet elevation.

- Maximum pump speed shall not exceed ______ RPM.

- Driver size shall be limited to _______ HP maximum.

- Liquid pumped is _______ with a maximum temperature of ___ deg. F.

PART 2, PRODUCTS

  - PUMPS

- Manufacturers

- Pump(s) shall be the product of Fairbanks Nijhuis.

- Manufacturer shall have installations of like or similar application with a minimum of 5 years service for this pump size.

- Design

- Rotation

- The pump will be counterclockwise rotation when viewed from the driver end looking at the pump.

- Impeller

- The impeller shall be of bronze construction conforming to ASTM B584, C83600.  They shall be of one-piece construction, single suction, enclosed ____-vane, and radial flow design.  The waterways through the impeller shall have extremely smooth contours, devoid of sharp corners, so as to promote maximum efficiency.

- The impeller is to be balanced and secured to the shaft by means of a stainless steel drive collet for bowl shafts 1-15/16” diameter and smaller.  For bowl shafts larger than 1-15/16” impellers shall be secured to the shaft using a combination of a thrust washer, key and/or snap rings.

- Impellers shall be adjustable by means of a top shaft-adjusting nut.

- Bowls

- The bowls shall be made of close-grained cast iron conforming to ASTM A48 CL30.  Castings shall be free from blowholes, sand holes and shall be accurately machined and fitted to close dimensions.

- Bowls 8” and above shall be flange connected.  Bowls below 8” nominal diameter may use either flanged or threaded connections.

- Bowls shall be designed with smooth passages to ensure efficient operation and their interior shall be coated with Tnemec N140 Pota-Pox Plus, or equal.

- The casing shall be hydrostatically tested to 1.5 times the design head or 1.25 times the shutoff head whichever is greater.

- Impeller Shaft

- Impeller shaft shall be of stainless steel construction conforming to ASTM A582 (416 stainless steel).

- The shaft shall be supported by bronze or neoprene bearings located on both sides of each impeller.

- Impeller shaft coupling shall be of stainless steel construction conforming to ASTM A582 (416 stainless steel).

- Wear Rings

- Wear rings shall be provided on both the impellers and bowls on bowls of nominal diameter of 8” or larger so that clearances can be maintained throughout the life of the rings and minimize recirculation.  Bowls of 6” and 7” nominal diameter shall incorporate bowl wear rings only.

- Impeller wear rings shall be of the radial-type.

- Bowl wear rings shall be of the radial-type.

- Wear rings shall be attached to the impellers and bowls using an interference fit and Loctite.

- Wear rings shall be bronze conforming to ASTM, B505 C93200.

- Column

- Total length of discharge column shall be ___ feet, ____ inches.

- Column pipe shall be not less than ___ inches inside diameter and weigh not less than ___ pounds per foot.

- Column pipe in sizes 4” through 12” diameter shall be furnished in interchangeable sections not over ten feet in length, and shall be connected with threaded, sleeve-type couplings.  Column pipe 14” diameter and larger shall be flanged and furnished in interchangeable sections not over ten feet in length.

- Threaded column sections shall be connected with threaded, sleeve-type couplings.  Column joints are to be butted to insure perfect column alignment after assembly.

- Lineshafts

- Lineshafting shall be of ample size to transmit the torque and operate the pump without distortion or vibration.

- Lineshafting shall be made of carbon steel conforming to AISI 1045 and be furnished in interchangeable sections not over ten feet in length.

- Lineshafting shall be coupled with extra-strong threaded steel couplings machined from solid bar steel.

- An enclosing tube shall be provided to house the lineshaft.  It shall be of extra-strong ASTM A120, Schedule 80 pipe construction and furnished in interchangeable sections not over five feet in length.  Each end of the enclosing tube shall be machined to receive a bronze connector bearing.

- Enclosing tube connector bearings shall be of bronze material conforming to ASTM B505 C93200 material.

- Units with overall lengths exceeding 30 feet shall incorporate an enclosing tube stabilizer for each additional 50 feet of the tube assembly.

- Discharge Head Assembly (above ground, packed box)

- The pump discharge head shall be of the above ground type of either cast iron or fabricated steel construction with an ANSI 125# discharge flange.

- The discharge head shall be of sufficient design to support the entire weight of the pump and driver.

- If the application uses a variable frequency drive, the discharge head shall be fabricated steel and specifically designed to elevate the discharge head natural frequency above the operating speed.

- A drive shaft of the same material as the lineshaft shall extend through the sealing assembly of the discharge head and be coupled to a vertical hollow shaft driver.

- The shaft sealing assembly shall consist of a bronze tension nut, a suitable oiler and oil reservoir to ensure proper lubrication for the bearings when the pump is in operation.  The oiler shall be furnished with a ___ volt solenoid for automatic operation.

- Discharge head openings shall be fitted with guards to prevent access to the rotating shaft and/or coupling.

OR

- Discharge Head Assembly (below ground, packed box)

- The pump discharge shall be of the below ground construction and consist of a driver mounting-base, underground elbow and riser pipe.

- The driver mounting-base shall be of sufficient design to support the entire weight of the pump and driver.

- If the application uses a variable frequency drive, the mounting-base shall be fabricated steel and specifically designed to elevate the mounting-base natural frequency above the operating speed.

- The underground elbow shall be of fabricated steel and have an ANSI 125# discharge flange.

- A driveshaft of the same material as the lineshaft shall extend through the sealing assembly of the driver-mounting base and be coupled to a vertical hollow shaft driver.

- The shaft sealing assembly shall consist of a bronze tension nut, a suitable oiler and oiler reservoir to ensure proper lubrication for the bearings when the pump is in operation.  The oiler shall be furnished with a ___ bolt solenoid for automatic operation.

- Driver mounting-base shall be fitted with guards to prevent access to the rotating shaft and/or coupling.

- Vibration Limitations (Field)

- The limits of vibration as set forth in the standards of the Hydraulic Institute shall govern.

- Testing

- A certified factory hydrostatic and performance test shall be performed on each bowl assembly in accordance with Hydraulic Institute Standards, latest edition.  Tests shall be sufficient to determine the curves of head, input horsepower, and efficiency relative to capacity from shutoff to 150% of design flow.  A minimum of six points, including shutoff, shall be taken for each test.  At least one point of the six shall be taken as near as possible to each specified condition.

- Results of the performance tests shall be certified by a Registered Professional Engineer and submitted for approval before final shipment.